Mock Document 1 — Technician Notes (AHU-04)

File name: Technician Notes AHU-04.txt (mock)

Technician Notes — Asset AHU-04
Facility: River Valley Medical Center — East Wing Surgical Pavilion
Asset ID: AHU-04
Date: 2025-09-15
Technician: J. Morales, HVAC Specialist

Summary of Visit:

- Reason for Call: Quarterly preventive maintenance (PM-09) + follow-up on noise complaint from Surgical OR 3.

- Observations:

  - Found AHU-04 access panel showing vibration wear on hinges.

  - Filter differential pressure: 1.5 in. w.c. (limit 2.0). Filters approaching replacement threshold.

  - Coil face moderately dusty; requires cleaning at next PM.

  - Fan belt tension below spec; visible fraying at edges.

  - Bearing noise audible during ramp-up; suspect lubrication overdue.

  - Motor amps at 92% of nameplate during peak demand.

- Actions Taken:

  - Re-tensioned belt; noted need for replacement within 30 days.

  - Lubricated motor bearings; noise reduced but still present at startup.

  - Tightened loose hinge bolts on access panel.

  - Logged filter differential pressure in CMMS.

- Recommendations:

  - Schedule belt replacement (WO #347892) before 2025-10-15.

  - Replace filters during next PM cycle or sooner if DP >1.8 in. w.c.

  - Clean cooling coil during winter shutdown (requires access scaffold).

  - Continue monitoring motor amperage; may be nearing end-of-life.

Additional Notes: - Infection Control notified prior to maintenance; negative pressure maintained. - Coordinated with OR Nurse Manager; no disruption to scheduled cases. - Uploaded photos of belt wear and motor nameplate to CMMS.

Technician Signature: J. Morales
Supervisor Review: Pending

End of Technician Notes (AHU-04)